Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This Product MasterSpec Section is licensed by ARCOM to Haworth, Inc. ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text, and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, ARCOM or The American Institute of Architects (AIA).  Neither AIA nor ARCOM are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user.  A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Haworth, Inc., 1 Haworth Center, Holland, MI 49423;  Phone: (616) 393-3000; Fax (616) 393-1560; Website: www.haworth.com/floors; Email: sue.borr@haworth.com.

For information about MasterSpec contact ARCOM at (800) 424-5080 or visit www.MasterSpec.com.

SECTION 096900 - ACCESS FLOORING

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

SUMMARY

Section Includes:

Access-flooring panels and understructure.

Floor panel coverings.

ACTION SUBMITTALS

Product Data:  For each type of product.

LEED Submittals:

Retain "Credit MR 4" subparagraph below if recycled content in system components is required for LEED Credit MR 4.

Credit MR 4:  Manufacturers' product data for system components, including printed statement of recycled material content.

"Product Data for Credit IEQ 4.1" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements for pedestal installation adhesives.

Product Data for Credit IEQ 4.1:  For pedestal-installation adhesives, documentation including printed statement of VOC content.

"Product Data for Credit IEQ 4.3" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements for pedestal-installation adhesives.

Product Data for Credit IEQ 4.3:  For pedestal-installation adhesives, documentation including printed statement of VOC content.

"Product Data for Credit IEQ 4.3" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements for floor panel coverings.

Product Data for Credit IEQ 4.3:  For floor panel coverings, documentation from an independent testing agency indicating compliance with the FloorScore Standard.

"Product Data for Credit IEQ 4.4" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS.

Product Data for Credit IEQ 4.4:  For particleboard used in steel-encapsulated, wood-core panels, documentation indicating that product contains no urea formaldehyde.

"Laboratory Test Reports for Credit IEQ 4" Subparagraph below applies to LEED for Schools.

Laboratory Test Reports for Credit IEQ 4:  For [access-flooring system with integral finishes] [pedestal-installation adhesives] [and] [particleboard used in steel-encapsulated, wood-core panels], documentation indicating that products comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

Shop Drawings:  Include layout, details, sections, and relationship to adjoining Work.

Samples:  For each type of product and exposed finish.

INFORMATIONAL SUBMITTALS

Product test reports.

Seismic Design Calculations:  For seismic design of access-flooring systems including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

MAINTENANCE MATERIAL SUBMITTALS

Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Flooring Panels:  [TecCrete 1250 & 1500 FBPX-XB00] [TecCrete 1500SL, 2000 & 2500 FBPX-XC00].  Provide <Insert number>.

For Haworth base component FBB in sub-paragraph below, "XX" indicates tube length, and "X" indicates seismic rating from 0 to 5.

Pedestals:  [TecCrete Field Head FBHA-06-F] [TecCrete Perimeter Head FBHA-06-P] [Base FBB-XX-X].  Provide <Insert number>.

Stringers:  [TecCrete Stringer 24-inches FBAX-24-S] [TecCrete Stringer 48-inches FBAX-48-S].  Provide <Insert number>.

QUALITY ASSURANCE

Manufacturer Qualifications: ISO 9001 and ISO 13001 certified.

Mockups:  Build mockups to verify selections made under Sample submittals to demonstrate aesthetic effects and to set quality standards for materials and execution.

Build mockup of typical access-flooring assembly as shown on Drawings.  Size to be an area no fewer than [five] <Insert number> floor panels in length by [five] <Insert number> floor panels in width.

Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing.

Retain subparagraph below if the intention is to make an exception to the default requirement in Section 014000 "Quality Requirements" for demolishing and removing mockups.

Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products.  For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

PERFORMANCE REQUIREMENTS

Retain "Seismic Performance" Paragraph below for projects requiring seismic design.  Delete paragraph if performance requirements are indicated on Drawings.  Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions.  Coordinate requirements with structural engineer.

Seismic Performance:  Access flooring shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Loads in "Structural Performance" Paragraph below are examples only; revise to suit Project.

When specifying the Haworth TecCrete 1250 system, retain "Structural Performance" paragraph and related sub-paragraphs below.  Delete "Structural Performance" paragraph and related sub-paragraphs below when specifying Haworth TecBase 1250 or TecBase 1500 systems.

Structural Performance:  According to testing procedures in CISCA's "Recommended Test Procedures for Access Floors":

Concentrated Loads:  1250 lbf (5560 N) with the following deflection and permanent set:

Top-Surface Deflection:  0.10 inch (2.54 mm).

Permanent Set:  0.010 inch (0.25 mm).

Ultimate Loads:  1800 lbf (8006 N) <Insert value>.

Rolling Loads:  With local or overall deformation not to exceed 0.040 inch (1.02 mm).

"CISCA Wheel 1" Subparagraph below simulates low-repetition, small-wheel loads; "CISCA Wheel 2" Subparagraph simulates high-repetition, large-wheel loads.

CISCA Wheel 1:  10 passes at 1200 lbf (5338 N).

CISCA Wheel 2:  10,000 passes at 800 lbf (3559 N).

Stringer Load Test:  450 lbf (2002 N) at center of span with a permanent set not to exceed 0.010 inch (0.25 mm).

Pedestal Axial Load Test:  5000 lbf (22,240 N).

Verify, with authorities having jurisdiction, requirements for pedestal overturning moment in seismic zones.

Pedestal Overturning Moment Test:  [1000 lbf x inches (113 N x meters)] when bonded to clean concrete slab.

Uniform Load Test:  600 lbf/sq. ft. (28.8 kPa) with a maximum top surface deflection not to exceed 0.040 inch (1.02 mm) and a permanent set not to exceed 0.010 inch (0.25 mm).

Drop Impact Load Test:  150 lb (68.0 kg).

When specifying the Haworth TecBase 1250 system, retain "Structural Performance" paragraph and related sub-paragraphs below.  Delete "Structural Performance" paragraph and related sub-paragraphs below when specifying Haworth TecCrete 1250 or TecBase 1500 systems.

Structural Performance:  Provide access-flooring systems capable of complying with the following performance requirements according to testing procedures in CISCA's "Recommended Test Procedures for Access Floors":

Concentrated Loads:  1250 lbf (5560 N) with the following deflection and permanent set:

Insert requirements for bottom-surface deflection if required.

Top-Surface Deflection:  0.10 inch (2.54 mm).

Permanent Set:  0.010 inch (0.25 mm).

Ultimate Loads:  1800 lbf (8007 N).

Loads specified in "Rolling Loads" Subparagraph below can cause failure in panels with insufficient concentrated- and ultimate-load capability; coordinate loads with panel capabilities specified above.

Rolling Loads:  With local or overall deformation not to exceed 0.040 inch (1.02 mm).

"CISCA Wheel 1" Subparagraph below simulates low-repetition, small-wheel loads similar to equipment move-in on dollies; "CISCA Wheel 2" Subparagraph simulates high-repetition, large-wheel loads similar to recurring office cart traffic.

CISCA Wheel 1:  10 passes at 1200 lbf (5338 N).

CISCA Wheel 2:  10,000 passes at 800 lbf (3559 N).

Retain "Stringer Load Testing" subparagraph below if stringer system is selected.

Stringer Load Test:  450 lbf (2002 N) at center of span with a permanent set not to exceed 0.010 inch (0.25 mm).

Pedestal Axial Load Test:  5000 lbf (22,240 N).

Verify, with authorities having jurisdiction, requirements for pedestal overturning moment in seismic zones.  Coordinate with pedestals retained.

Pedestal Overturning Moment Test:  1000 lbf x inches (113 N x meters) when bonded to clean concrete slab.

Drop Impact Load Test:  150 lb (68.0 kg).

When specifying the Haworth TecBase 1500 system, retain "Structrual Performance" paragraph and related sub-paragraphs below.  Delete "Structural Performance" paragraph and related sub-paragraphs below when specifying Haworth TecCrete 1250 or TecBase 1250 systems.

Structural Performance:  Provide access-flooring systems capable of complying with the following performance requirements according to testing procedures in CISCA's "Recommended Test Procedures for Access Floors":

Concentrated Loads:  1500 lbf (6672 N) with the following deflection and permanent set:

Insert requirements for bottom-surface deflection if required.

Top-Surface Deflection:  0.10 inch (2.54 mm).

Permanent Set:  0.010 inch (0.25 mm).

Ultimate Loads:  2500 lbf (11,121 N).

Loads specified in "Rolling Loads" Subparagraph below can cause failure in panels with insufficient concentrated- and ultimate-load capability; coordinate loads with panel capabilities specified above.

Rolling Loads:  With local or overall deformation not to exceed 0.040 inch (1.02 mm).

"CISCA Wheel 1" Subparagraph below simulates low-repetition, small-wheel loads similar to equipment move-in on dollies; "CISCA Wheel 2" Subparagraph simulates high-repetition, large-wheel loads similar to recurring office cart traffic.

CISCA Wheel 1:  10 passes at 1500 lbf (6672 N).

CISCA Wheel 2:  10,000 passes at 1250 lbf (5560 N).

Retain "Stringer Load Test" subparagraph below if a stringer system is sleected.

Stringer Load Test:  450 lbf (2002 N) at center of span with a permanent set not to exceed 0.010 inch (0.25 mm).

Pedestal Axial Load Test:  5000 lbf (22,240 N).

Verify, with authorities having jurisdiction, requirements for pedestal overturning moment in seismic zones.  Coordinate with pedestals retained.

Pedestal Overturning Moment Test:  1000 lbf x inches (113 N x meters) when bonded to clean concrete slab.

Drop Impact Load Test:  150 lb (68.0 kg).

Structural Performance:  Provide access-flooring systems capable of complying with the following performance requirements according to testing procedures in CISCA's "Recommended Test Procedures for Access Floors":

Concentrated Loads:  1500 lbf (6672 N) with the following deflection and permanent set:

Insert requirements for bottom-surface deflection if required.

Top-Surface Deflection:  0.10 inch (2.54 mm).

Permanent Set:  0.010 inch (0.25 mm).

Ultimate Loads:  2500 lbf (11,121 N).

Loads specified in "Rolling Loads" Subparagraph below can cause failure in panels with insufficient concentrated- and ultimate-load capability; coordinate loads with panel capabilities specified above.

Rolling Loads:  With local or overall deformation not to exceed 0.040 inch (1.02 mm).

"CISCA Wheel 1" Subparagraph below simulates low-repetition, small-wheel loads similar to equipment move-in on dollies; "CISCA Wheel 2" Subparagraph simulates high-repetition, large-wheel loads similar to recurring office cart traffic.

CISCA Wheel 1:  10 passes at 1500 lbf (6672 N).

CISCA Wheel 2:  10,000 passes at 1250 lbf (5560 N).

Retain "Stringer Load Testing" subparagraph below if stringer system is selected.

Stringer Load Test:  450 lbf (2002 N) at center of span with a permanent set not to exceed 0.010 inch (0.25 mm).

Pedestal Axial Load Test:  5000 lbf (22,240 N).

Verify, with authorities having jurisdiction, requirements for pedestal overturning moment in seismic zones.  Coordinate with pedestals retained.

Pedestal Overturning Moment Test:  1000 lbf x inches (113 N x meters) when bonded to clean concrete slab.

Drop Impact Load Test:  150 lb (68.0 kg).

Structural Performance:  Provide access-flooring systems capable of complying with the following performance requirements according to testing procedures in CISCA's "Recommended Test Procedures for Access Floors":

Concentrated Loads:  2000 lbf (8896 N) with the following deflection and permanent set:

Insert requirements for bottom-surface deflection if required.

Top-Surface Deflection:  0.10 inch (2.54 mm).

Permanent Set:  0.010 inch (0.25 mm).

Ultimate Loads:  2800 lbf (12.455 N).

Loads specified in "Rolling Loads" Subparagraph below can cause failure in panels with insufficient concentrated- and ultimate-load capability; coordinate loads with panel capabilities specified above.

Rolling Loads:  With local or overall deformation not to exceed 0.040 inch (1.02 mm).

"CISCA Wheel 1" Subparagraph below simulates low-repetition, small-wheel loads similar to equipment move-in on dollies; "CISCA Wheel 2" Subparagraph simulates high-repetition, large-wheel loads similar to recurring office cart traffic.

CISCA Wheel 1:  10 passes at 1500 lbf (6672 N).

CISCA Wheel 2:  10,000 passes at 1250 lbf (5560 N).

Retain "Stringer Load Testing" subparagraph below if stringer system is selected.

Stringer Load Test:  450 lbf (2002 N) at center of span with a permanent set not to exceed 0.010 inch (0.25 mm).

Pedestal Axial Load Test:  5000 lbf (22,240 N).

Verify, with authorities having jurisdiction, requirements for pedestal overturning moment in seismic zones.  Coordinate with pedestals retained.

Pedestal Overturning Moment Test:  1000 lbf x inches (113 N x meters) when bonded to clean concrete slab.

Drop Impact Load Test:  150 lb (68.0 kg).

Structural Performance:  Provide access-flooring systems capable of complying with the following performance requirements according to testing procedures in CISCA's "Recommended Test Procedures for Access Floors":

Concentrated Loads:  2500 lbf (11,121 N) with the following deflection and permanent set:

Insert requirements for bottom-surface deflection if required.

Top-Surface Deflection:  0.10 inch (2.54 mm).

Permanent Set:  0.010 inch (0.25 mm).

Ultimate Loads:  3100 lbf (13,789 N).

Loads specified in "Rolling Loads" Subparagraph below can cause failure in panels with insufficient concentrated- and ultimate-load capability; coordinate loads with panel capabilities specified above.

Rolling Loads:  With local or overall deformation not to exceed 0.040 inch (1.02 mm).

"CISCA Wheel 1" Subparagraph below simulates low-repetition, small-wheel loads similar to equipment move-in on dollies; "CISCA Wheel 2" Subparagraph simulates high-repetition, large-wheel loads similar to recurring office cart traffic.

CISCA Wheel 1:  10 passes at 2000 lbf (8896 N).

CISCA Wheel 2:  10,000 passes at 2000 lbf (8896 N).

Retain "Stringer Load Testing" subparagraph below if stringer system is selected.

Stringer Load Test:  450 lbf (2002 N) at center of span with a permanent set not to exceed 0.010 inch (0.25 mm).

Pedestal Axial Load Test:  5000 lbf (22,240 N).

Verify, with authorities having jurisdiction, requirements for pedestal overturning moment in seismic zones.  Coordinate with pedestals retained.

Pedestal Overturning Moment Test:  1000 lbf x inches (113 N x meters) when bonded to clean concrete slab.

Drop Impact Load Test:  150 lb (68.0 kg).

Fire Performance:

Surface-Burning Characteristics:  Comply with ASTM E 84; testing by a qualified testing agency.  Identify products with appropriate markings of applicable testing agency.

Flame-Spread Index:  25 or less.

Smoke-Developed Index:  50 or less.

Combustion Characteristics:  ASTM E 136.

Retain "Low-Emitting Materials" Paragraph below if required for LEED for Schools Credit IEQ 4.

Low-Emitting Materials:  Flooring system shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

FLOOR PANELS

Floor Panels, General:  Provide modular panels interchangeable with other field panels without disturbing adjacent panels or understructure.

Size:  Nominal [24 by 24 inches (610 by 610 mm)] <Insert dimensions>.

Attachment to Understructure:  [Bolted] [By gravity].

In "Cementitious-Core Steel Panels," "Wood-Core Steel Panels," and "Unfilled Steel Panels," paragraphs below, retain type of panel construction required.  If retaining more than one panel type below, indicate location of each on Drawings or by inserts.

Cementitious-Core Steel Panels:  Fabricated from cold-rolled steel sheet, with the die-cut flat top sheet and die-formed and stiffened bottom pan welded together, and with metal surfaces protected against corrosion by manufacturer's standard factory-applied finish.  Fully grout internal spaces of completed units with manufacturer's standard cementitious fill.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product:  Subject to compliance with requirements, provide Haworth, Inc.; [TecCrete 1250] [TecCrete 1500] [TecCrete 1500SL] [TecCrete 2000] [TecCrete 2500] or comparable product by one of the following:

ASM Modular Systems, Inc.

Bergvik North America, Inc.

Camino Modular Systems, Inc.

Computer Environments, Inc.

Tate Access Floors, Inc.

<Insert manufacturer's name>.

If retaining "Wood-Core Steel Panels" Paragraph below and low-emitting materials are required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.4, retain first option after verifying availability of panels that comply with requirement.  Retain second option if required for LEED for Schools Credit IEQ 4.

Wood-Core Steel Panels:  Fabricated with 1-inch- (25-mm-) thick particleboard core[, made without urea formaldehyde][, that complies with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers,"] laminated to top and bottom steel face sheets, with metal surfaces protected against corrosion by manufacturer's standard factory-applied finish, and with a flame-spread index of 25 or less according to ASTM E 84.  Provide core edges enclosed with upturned, die-formed, bottom-sheet edge or with perimeter steel channel welded to top sheet and welded or bonded to bottom sheet.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers:  Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

ASM Modular Systems, Inc.

Bergvik North America, Inc.

Camino Modular Systems, Inc.

Computer Environments, Inc.

Tate Access Floors, Inc.

<Insert manufacturer's name>.

Unfilled Steel Panels:  Fabricated from cold-rolled steel sheet, with the die-cut flat top sheet and die-formed and stiffened bottom pan welded together, and with metal surfaces protected against corrosion by manufacturer's standard factory-applied finish.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product:  Subject to compliance with requirements, provide Haworth, Inc.; [TecCrete 1250] [TecCrete 1500] [TecCrete 1500SL] [TecCrete 2000] [TecCrete 2500] or comparable product by one of the following:

ASM Modular Systems, Inc.

Camino Modular Systems, Inc.

Computer Environments, Inc.

Tate Access Floors, Inc.

<Insert manufacturer's name>.

Solid Panels:  Flat, solid top surface.

Retain "Perforated Panels" and "Grates" subparagraphs below if required.  Perforated panels and grates are used for delivering large amounts of air to heavy equipment rooms such as telecommunications switch centers, but not for normal office ventilation.

Perforated Panels:  Perforated top surface with [holes] [slots] of number, spacing, and size standard with manufacturer to produce a nominal open area of [23] [24] [25] <Insert number> percent.[  Provide mechanical dampers with each panel unit.]

Quantity:  [As shown on Drawings] <Insert number>.

Finish:  [Manufacturer's standard] [To match solid panels] <Insert finish>.

Grates:  Grating ribs arranged in manufacturer's standard pattern to produce a nominal open area of [45] [50] [56] <Insert number> percent.[$ds~Provide mechanical dampers with each panel unit.]

Quantity:  [As shown on Drawings] <Insert number>.

Finish:  [Manufacturer's standard] [To match solid panels] <Insert finish>.

Exposed-Concrete-Surface Panels:  Fabricated with bottom pan that is die formed from metallic-coated steel sheet and filled with lightweight concrete that is reinforced and bonded to pan by shear ties.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product:  Subject to compliance with requirements, provide Haworth, Inc.; [TecCrete 1250] [TecCrete 1500] [TecCrete 1500SL] [TecCrete 2000] [TecCrete 2500] or comparable product by one of the following:

<Insert manufacturer's name>.

UNDERSTRUCTURE

Pedestals:  Assembly consisting of base, column with provisions for height adjustment, and head (cap); made of steel.

Retain first subparagraph below if seismic pedestals are required.

Provide pedestals designed for use in seismic applications.

Base:  Square or circular base with not less than [16 sq. in. (103 sq. cm)] <Insert dimension> of bearing area.

Column:  Of height required to bring finished floor to elevations indicated.  Weld to base plate.

Provide vibration-proof leveling mechanism for making and holding fine adjustments in height over a range of not less than [2 inches (51 mm)] <Insert dimension>.

Head:  Designed to support the panel system indicated.

Delete "Stringer Systems" Paragraph below for stringerless installation.

Stringer Systems:  Modular steel stringer systems designed to bolt to pedestal heads with manufacturer's standard galvanized or corrosion-resistant paint finish.

FLOOR PANEL COVERINGS

Many types of standard finish flooring may be applied over access-flooring panels.  Retain this article for factory-applied, access-flooring finishes.

Floor panel covering options in paragraphs below apply only to Haworth's TecBase.  The TecCrete product is always provided bare, without factory-applied floor coverings on traffic surfaces.  It can be installed and used bare as well.

Retain "FloorScore Compliance" Paragraph below if required for LEED-NC, LEED-CS, or LEED-CI Credit IEQ 4.3; before retaining, verify availability of materials that comply.

FloorScore Compliance:  Floor panel coverings shall comply with requirements of FloorScore Standard.

Retain first option in "High-Pressure Plastic Laminate" Paragraph below for 0.118-inch (3-mm) thickness; retain second option for 0.059-inch (1.5-mm) thickness.

High-Pressure Plastic Laminate:  Factory applied, NEMA LD 3, High-Wear type, [Grade HDH] [Grade HDM]; fabricated in one piece to cover each panel face with [integral trim] [applied perimeter plastic] edging.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers:  Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Formica Corporation.

Panolam Industries.

<Insert manufacturer's name>.

Electrical Resistance:  Average no less than 1 megohm and no more than 20,000 megohms when installed floor coverings are surface-to-ground tested according to NFPA 99.

Colors, Textures, and Patterns:  [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert colors, textures, and patterns>.

Retain first option in "Conductive High-Pressure Plastic Laminate" Paragraph below for 0.118-inch (3-mm) thickness; retain second option for 0.059-inch (1.5-mm) thickness.

Conductive High-Pressure Plastic Laminate:  Factory applied, NEMA LD 3, High-Wear type, [Grade HDH] [Grade HDM]; fabricated in one piece to cover each panel face with [integral trim] [applied perimeter plastic] edging.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers:  Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Panolam Industries.

<Insert manufacturer's name>.

Electrical Resistance:  Average no less than 25,000 ohms and no more than 1 megohm when installed floor coverings are surface-to-ground tested according to ASTM F 150 with 100-V applied voltage.

Colors, Textures, and Patterns:  [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert colors, textures, and patterns>.

Vinyl Tile:  Factory applied, ASTM F 1700, Class I (Monolithic Vinyl Tile), Type A (Smooth Surface), [static dissipative] [conductive], fabricated in one piece to cover panel face with [monolithic] [applied perimeter plastic] edging.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers:  Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Flexco, Inc.

VPI Corporation.

<Insert manufacturer's name>.

Retain first option in "Electrical Resistance" Subparagraph below for static-dissipative tile; retain second option for conductive tile.

Electrical Resistance:  Average no less than [1 megohm and no more than 1000 megohms] [25,000 ohms and no more than 1 megohm] when installed floor coverings are surface-to-ground tested according to ASTM F 150 with 100-V applied voltage.

Colors, Textures, and Patterns:  [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert colors, textures, and patterns>.

FABRICATION

Fabrication Tolerances:

Size:  Plus or minus 0.020 inch (0.50 mm) of required size.

Squareness:  Plus or minus 0.015 inch (0.38 mm) between diagonal measurements across top of panel.

Flatness:  Plus or minus 0.035 inch (0.89 mm), measured on a diagonal on top of panel.

Cutouts:  Fabricate cutouts in floor panels for cable penetrations and service outlets.  Provide reinforcement or additional support, if needed, to make panels with cutouts comply with structural performance requirements.  Where indicated, fit cutouts with manufacturer's standard grommets.

Number, Size, Shape, and Location:  [As indicated.] [As specified in Section 012100 "Allowances" and Section 012200 "Unit Prices."]

ACCESSORIES

Adhesives:  Manufacturer's standard adhesive for bonding pedestal bases to subfloor.

Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.  VOC content limit is that for multipurpose construction adhesives.

Adhesive shall have a VOC content of 70 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools Credit IEQ 4; coordinate with products.

Adhesive shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

Retain "Service Outlets" Paragraph below if required.  Designs of outlets differ among manufacturers; if retaining, revise to suit Project.

Service Outlets:  Standard UL-listed and -labeled assemblies, for recessed mounting flush with top of floor panels; for power, communication, and signal services; and complying with the following requirements:

Structural Performance:  Cover capable of supporting a 300-lbf (1334-N) concentrated load.

Cover and Trim Ring Type:  Painted steel cover with opening for passage of cables when cover is closed and including trim ring frame for use with steel box assembly for mounting electrical receptacles and/or communications outlets.

Location:  In center of panel quadrant unless otherwise indicated.

Retain one of two "Receptacles and Wiring" subparagraphs below.

Receptacles and Wiring:  Electrical receptacles and wiring for service outlets are specified elsewhere.

Receptacles and Wiring:  Heavy-duty duplex, two-pole, three-wire grounding, [20 A] [15 A], 125 V, NEMA WD 6, Configuration 5-20R unless otherwise indicated.

Number of Receptacles for Outlet:  [One] [Two] [Three] [Four] [Five] [Six] [Seven] [Eight] <Insert number>.

[Factory wired for hard wiring in field with armored cable or conduit] [Power-in modular connectors, built into outlet housing, for use with modular power distribution assemblies which are listed in compliance with UL 183, Safety Standard for Manufactured Wiring Systems].

Occupant Adjustable Diffusers:  Manufacturer's standard round diffusers, [5 inches (127 mm)] [8 inches (203 mm)] <Insert dimension> in diameter, formed from [aluminum] [engineered polymer] [polycarbonate plastic] to produce a removable one-piece unit complete with diffuser, manually adjustable flow regulator, dirt and dust receptacle, trim ring, and underfloor compression mounting ring:

Air-Distribution Characteristics:  [88 cfm (41.5 L/s)] <Insert value> at [0.096-inch (24-Pa)] <Insert value> static pressure and a maximum noise criterion rating of [15] <Insert number>.

Structural Performance:  Capable of supporting a [600-lbf (2669-N)] <Insert value> concentrated load.

Floor Grilles:  Standard load-bearing grilles formed from [aluminum] [polycarbonate plastic] to produce removable one-piece unit precisely fitted in factory-prepared openings of standard field panels, [with adjustable/removable] [without] dampers:

Air-Distribution Characteristics:  468 cfm at 0.10-inch wg (221 L/s at 25-Pa) static pressure.

Structural Performance:  Capable of supporting a 1000-lbf (4448-N) concentrated load.

Plenum-Wall Brush Grommets:  Self-sealing cable brush grommet with [4-by-13-inch (102-by-330-mm) rectangular] [3-inch (76-mm) round] [5-inch (127-mm) round] <Insert dimension(s)> usable area for passage of power and signal cables through plenum walls.

Cavity Dividers:  Provide manufacturer's standard metal dividers located where indicated to divide underfloor cavities.

Closures:  Where underfloor cavity is not enclosed by abutting walls or other construction, provide metal-closure plates with [manufacturer's standard finish] <Insert finish>.

Retain "Ramps," "Steps," and "Railings" paragraphs below if required for access from adjacent flooring.  Indicate locations and details on Drawings.

Ramps:  Not steeper than 1:12, with raised-disc or textured rubber or vinyl-tile floor coverings, and of same materials, performance, and construction requirements as access flooring.

Steps:  Size and arrangement indicated with floor coverings to match access flooring.  Apply nonslip aluminum nosings to treads unless otherwise indicated.

Railings:  Standard extruded-aluminum railings at ramps and open-sided perimeter of access flooring where indicated.  Include handrail, intermediate rails, posts, brackets, end caps, wall returns, wall and floor flanges, plates, and anchorages where required.

Retain subparagraph below, or delete and insert performance requirements here.

Provide railings that comply with structural performance requirements specified in [Section 055213 "Pipe and Tube Railings."] [Section 057300 "Decorative Metal Railings."]

For computer rooms to comply with NFPA 75, retain option in "Panel Lifting Device" Paragraph below.

Panel Lifting Device:  Panel manufacturer's standard portable lifting device for each type of panel required[ for each computer room].

EXECUTION

PREPARATION

Examine substrates for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.  Proceed with installation only after unsatisfactory conditions have been corrected.

Lay out floor panel installation to keep the number of cut panels at floor perimeter to a minimum.  Avoid using panels cut to less than 6 inches (152 mm).

Locate each pedestal, complete any necessary subfloor preparation, and vacuum subfloor to remove dust, dirt, and construction debris before beginning installation.

INSTALLATION

Install access-flooring system and accessories under supervision of access-flooring manufacturer's authorized representative to produce a rigid, firm installation that complies with performance requirements and is free of instability, rocking, rattles, and squeaks.

Delete "Adhesive Attachment of Pedestals" Paragraph below and insert paragraph for mechanical attachment of pedestals if bolted attachment of pedestal bases is required for seismic applications or where increased rigidity is needed.

Adhesive Attachment of Pedestals:  Set pedestals in adhesive, according to access-flooring manufacturer's written instructions, to provide full bearing of pedestal base on subfloor.

Install flooring panels securely in place, properly seated with panel edges flush.  Do not force panels into place.

Scribe perimeter panels to provide a close fit with adjoining construction with no voids greater than 1/8 inch (3 mm) where panels abut vertical surfaces.

Grounded Flooring Access Panel Systems:  Ground flooring system as recommended by manufacturer and as needed to comply with performance requirements for electrical resistance of floor coverings.  Not more than 10 ohms as measured without floor coverings.

Scribe and install [underfloor-cavity dividers] [and] [closures] to closely fit against subfloor and other adjacent surfaces, and seal with mastic.

Clean dust, dirt, and construction debris caused by floor installation, and vacuum subfloor area as installation of floor panels proceeds.

Retain first paragraph below for underfloor air distribution (UFAD) systems.

Seal underfloor air cavities at construction seams, penetrations, and perimeter to control air leakage, according to manufacturer's written instructions.

Install access flooring without change in elevation between adjacent panels and within the following tolerances:

Plus or minus [1/16 inch (1.5 mm)] [1/8 inch (3 mm)] <Insert dimension> in any 10-foot (3-m) distance.

Plus or minus [1/8 inch (3 mm)] [1/4 inch (6.5 mm)] <Insert dimension> from a level plane over entire access-flooring area.

Prohibit traffic on access flooring for 24 hours and removal of floor panels for [72] <Insert number> hours after installation to allow pedestal adhesive to set.

Replace access-flooring panels that are stained, scratched, or otherwise damaged or that do not comply with specified requirements.

END OF SECTION 096900